Laars Heating Systems Company – LT Series Models LT199

SECTION 223400 - FUEL-FIRED, DOMESTIC-WATER HEATERS

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes gas-fired, wall-hung, tankless domestic-water heaters.

ACTION SUBMITTALS

Product Data: For each type of product, include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

Sustainable Design Submittals:

Product Data for water heater compliance with ASHRAE's "Advanced Energy Design Guides."

Shop Drawings:  Include diagrams for power, signal, and control wiring.

INFORMATIONAL SUBMITTALS

Coordination Drawings: Equipment room drawing or BIM model, drawn to scale, on which the items described in this Section are shown and coordinated with all building trades.

Product Certificates: For each type of gas-fired, domestic-water heater.

Domestic-Water Heater Labeling: Certified and labeled by testing agency acceptable to authorities having jurisdiction.

Source quality-control reports.

Field quality-control reports.

Warranty: Standard warranty, shown below.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For fuel-fired, domestic-water heaters to include in emergency, operation, and maintenance manuals.

COORDINATION

Coordinate sizes and locations of concrete bases with actual equipment provided.

WARRANTY

Manufacturer’s Warranty: Manufacturer agrees to repair or replace components of fuel-fired, domestic-water heaters that fail in materials or workmanship within specified warranty period.  Where “prorated” is indicated, the heater manufacturer will cover the indicated percentage of cost or replacement parts. With “prorated” type, covered cost decreases as age of equipment increases.

Failures include, but are not limited to, the following:

Structural failures.

Faulty operation of controls.

Deterioration of metals, metal finishes, and other materials beyond normal use.

Warranty Periods: Limited warranty is effective as of the date of installation or 6 months after the date of manufacture, whichever is first.

Heat Exchanger Failure Due to Other Than Thermal Shock: 15 years, non-prorated in single family dwellings. 8 years, non-prorated in applications other than single-family dwelling.

Components Other Than Heat Exchanger:  5 years.

PRODUCTS

PERFORMANCE REQUIREMENTS

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by an NRTL, and marked for intended location and use.

ASHRAE/IES Compliance: Comply with efficiency requirements in ASHRAE 189.1, which supersede requirements in ASHRAE/IES 90.1.

Compliance:  ANSI Z21.10.3/CSA 4.3 for gas-fired, instantaneous, domestic water heaters for indoor application.

AHRI:  Heater Uniform Energy Factor shall be determined and listed by AHRI.

NSF/ANSI 372 Low Lead Compliance.

Energy Star Qualified.

GAS-FIRED, TANKLESS, DOMESTIC-WATER HEATERS

Basis-of-Design Product: Subject to compliance with requirements, provide Laars Heating Systems Company LT Series Tankless Water Heater, or comparable product by one of the following:

A. O. Smith Corporation

Bosch Thermotechnology Corporation

Bradford White Corporation

Rinnai Corporation

Source: Limitations:  Obtain domestic water heaters from single source from single manufacturer.

Standard:  ANSI Z21.10.3/CSA 4.3 for gas-fired, instantaneous, domestic water heaters for indoor application.

Heater Construction:

Stainless steel primary and secondary heat exchangers complying with NSF 372 barrier materials for potable water, without storage capacity.

Heater must be available in a standard configuration, and as a model with built-in recirculation pump and control logic.

Tappings: ¾-inch NPT cold water inlet, hot water outlet, recirculation connection (in models fitted for recirculation), and gas.

Pressure Rating: 150 psig (1035 kPa).

Heat Exchanger: Stainless steel.

Jacket: Metal, with enameled finish, or plastic.

Burner: For use with [natural gas] [propane gas] <insert fuel gas> fuel.

Automatic Ignition: Manufacturer’s proprietary system for automatic gas ignition.

Temperature Control: Adjustable thermostat with 185°F maximum water temperature to allow for residential or commercial use.

Control shall allow up to 16 heaters to be cascaded together including up to 2 recirc models.

Support: Bracket for wall mounting.:

Capacity and Characteristics:

Flow Rate: 5.1 gpm (0.32 L/s) at 77°F (43°C) temperature rise.

Temperature Setting: [125°F (52°C)] [140°F (60°C)] [180°F (82°C)] <insert temperature>.

Fuel Gas Demand: <Insert cfh (L/s)>

Fuel Gas Input: 199,000 Btu/h (58.3 kW).

Inlet Natural Gas Pressure: 3.5- to 10.5-in. wg (861 to 2584 Pa).

AHRI Certified Uniform Energy Factor:  0.96

UED Recovery Efficiency:  98 percent

CEE Tier 2.

Voltage:  120-V ac, single phase, 60 Hz.

Heater Intake and Exhaust Vent Piping:

Install flue-venting kit and combustion-air intake:

Intake air may be taken from the room, or ducted to the heater.  Air pipe material may be ABS, PVC, CPVC, galvanized steel, stainless steel, or polypropylene.  Air pipe diameter and length may be:

up to 60 equivalent feet of 2 inch diameter pipe.

up to 150 equivalent feet of 3 inch diameter pipe.

Exhaust vent is Category IV.  Vent pipe material in the U.S. must be stainless steel UL 1738, PVC sch 40 ULC S636 / ANSI/ASTM D1785, CPVC sch 40 UL1738 / ULC S636 / ANSI/ASTM F441, or polypropylene UL1738 / ULC S636.  Vent pipe material in Canada must be ULC S636 certified. Category IV vent pipe diameter and length may be:

up to 60 equivalent feet of 2 inch diameter pipe.

up to 150 equivalent feet of 3 inch diameter pipe.

Heater shall be allowed to be vented with up to 60 equivalent feet or 2 inch flexible polypropylene or up to 150 equivalent feet of 3 inch flexible polypropylene that is certified to UL-1738/ULC-S636, when room air is used, and installation of flexible pipe is vertical.

Comply with all heater manufacturer’s installation instructions.

SOURCE QUALITY CONTROL

Factory Tests: Test and inspect assembled domestic-water heaters.

Domestic-water heaters will be considered defective if they do not pass tests and inspections.

Assembled heater must be factory tested for safety and functionality; heater filled with water, fired throughout firing range, with all burner safety components proven. Results recorded for future reference.

Prepare test and inspection reports.

EXECUTION

DOMESTIC-WATER HEATER INSTALLATION

Install domestic-water heaters level and plumb, in accordance with layout drawings, original design, and referenced standards. Maintain manufacturer's recommended clearances. Arrange units so controls and devices needing service are accessible.

Install gas-fired, domestic-water heaters in accordance with NFPA 54.

Assemble and install any additional or optional heater trim.

Fill domestic water heaters with water.

Charge domestic-water expansion tanks with air to required system pressure.

PIPING CONNECTIONS

Comply with requirements for domestic-water piping specified in Section 221116 "Domestic Water Piping."

Comply with requirements for gas piping specified in Section 231123 "Facility Natural-Gas Piping."

Drawings indicate general arrangement of piping, fittings, and specialties.

Where installing piping adjacent to fuel-fired, domestic-water heaters, allow space for service and maintenance of water heaters. Arrange piping for easy removal of domestic-water heaters.

IDENTIFICATION

Identify system components. Comply with requirements for identification specified in Section 220553 "Identification for Plumbing Piping and Equipment."

FIELD QUALITY CONTROL

Testing Agency: Engage a qualified testing agency to perform tests and inspections.

Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Perform tests and inspections in accordance with manufacturer’s written instructions.

Tests and Inspections:

Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

Operational Test: After electrical circuitry has been energized, start units to confirm proper operation.

Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

Domestic-water heaters will be considered defective if they do not pass tests and inspections.

Prepare test and inspection reports.

DEMONSTRATION

Train owner's maintenance personnel to adjust, operate, and maintain the domestic-water heaters.

END OF SECTION 223400