Laars Model EV Electric Water Heater Specification

PART 1 – GENERAL

1.1 RELATED DOCUMENTS

- Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this section.

1.2 WORK INCLUDED

- Section includes electric water heater. The heater shall be fabricated, assembled, charged, and tested by one manufacturer.

1.3 SUBMITTALS

- Submit shop drawings, mechanical layout, flow schematics, and product data, as specified.  Include capacity data, installation manual, startup and service instructions, and spare/replacement parts lists.

1.4 QUALITY ASSURANCE AND COMPLIANCE

- Reference Standards

  - ETL Standard For Electric Booster and Commercial Storage Tank Water Heaters, Construction and Test of Electric Storage-Tank Water Heaters (R2014) [CSA C22.2#110:1994 Ed.5+G1;U2;U3]

  - NSF/ANSI 372 Low Lead Content.

  - ASME Boiler and Pressure Vessel Code Section IV HLW Stamp.

  - ASHRAE 90.1b Energy Efficiency Standard for Buildings.

- Each submittal shall be provided with documentation certifying that all materials, products, components, and test reports comply with the design requirements for this project.

- Furnish all equipment, materials, and accessories new and free from defects.

1.5 WARRANTY

- Manufacturer’s Warranty:  Manufacturer agrees to repair or replace components of tank that fail in materials or workmanship within specified warranty period.

- Warranty Period:

  - 10-Year limited tank warranty.

  - 6-Year limited electric element warranty.

  - 1-Year warranty for all other parts.

PART 2 – PRODUCTS

2.1 RATINGS

- Gallon Capacity:

  - Model EV0150:  150 gallons (568 liters)

  - Model EV0200:  200 gallons (757 liters)

  - Model EV0250:  250 gallons (947 liters)

  - Model EV0300:  300 gallons (1136 liters)

  - Model EV0400:  400 gallons (1514 liters)

  - Model EV0500:  500 gallons (1893 liters)

  - Model EV0600:  600 gallons (2272 liters)

  - Model EV0800:  800 gallons (3029 liters)

  - Model EV1000:  1000 gallons (3786 liters)

  - Model EV1250:  1250 gallons (4733 liters)

  - Model EV1500:  1500 gallons (5679 liters)

  - Model EV2000:  2000 gallons (7572 liters)

  - Model EV2500:  2500 gallons (9465 liters)

- Power and Recovery – Heaters shall be available with the following power and recovery ratings:

  - 15 kW (51,180 Btu/hr) – 62 gph (234 L/h) recovery at 100°F (56°C) rise

  - 18 kW (61,416 Btu/hr) – 74 gph (280 L/h) recovery at 100°F (56°C) rise

  - 30 kW (102,360 Btu/hr) – 123 gph (465 L/h) recovery at 100°F (56°C) rise

  - 36 kW (122,832 Btu/hr) – 148 gph (559 L/h) recovery at 100°F (56°C) rise

  - 45 kW (153,540 Btu/hr) – 185 gph (699 L/h) recovery at 100°F (56°C) rise

  - 54 kW (184,248 Btu/hr) – 221 gph (835 L/h) recovery at 100°F (56°C) rise

  - 60 kW (204,720 Btu/hr) – 246 gph (930 L/h) recovery at 100°F (56°C) rise

  - 72 kW (245,664 Btu/hr) – 295 gph (1115 L/h) recovery at 100°F (56°C) rise

  - 90 kW (307,080 Btu/hr) – 369 gph (1395 L/h) recovery at 100°F (56°C) rise

  - 108 kW (368,496 Btu/hr) – 443 gph (1675 L/h) recovery at 100°F (56°C) rise

  - 120 kW (409,440 Btu/hr) – 492 gph (1860 L/h) recovery at 100°F (56°C) rise

  - 135 kW (460,062 Btu/hr) –  554 gph (2094 L/h) recovery at 100°F (56°C) rise

  - 144 kW (491,328 Btu/hr) –  590 gph (2230 L/h) recovery at 100°F (56°C) rise

  - 162 kW (552,744 Btu/hr) –  664 gph (2510 L/h) recovery at 100°F (56°C) rise

  - 180 kW (614,160 Btu/hr) –  738 gph (2790 L/h) recovery at 100°F (56°C) rise

  - 216 kW (736,992 Btu/hr) –  886 gph (3349 L/h) recovery at 100°F (56°C) rise

  - 252 kW (859,824 Btu/hr) – 1033 gph (3905 L/h) recovery at 100°F (56°C) rise

  - 270 kW (921,240 Btu/hr) – 1107 gph (4184 L/h) recovery at 100°F (56°C) rise

  - 288 kW (982,656 Btu/hr) – 1181 gph (4464 L/h) recovery at 100°F (56°C) rise

  - 324 kW (1,105,488 Btu/hr) – 1327 gph (5016 L/h) recovery at 100°F (56°C) rise

  - 360 kW (1,228,320 Btu/hr) – 1476 gph (5579 L/h) recovery at 100°F (56°C) rise

- Heaters shall be available in the following voltages:

  - 15-60 kW models:

    - 208V single phase

    - 240V single phase

    - 277V single phase

    - 208V three phase

    - 240V three phase

    - 277V three phase

    - 380V three phase

    - 400V three phase

    - 415V three phase

    - 480V three phase

    - 600V three phase

  - 72-108 kW models:

    - 208V three phase

    - 240V three phase

    - 277V three phase

    - 380V three phase

    - 400V three phase

    - 415V three phase

    - 480V three phase

    - 600V three phase

- Operating Conditions:

  - Maximum water pressure = 150 psi (1034 kPa)

  - Maximum water temperature = 180°F (82°C)

2.2 CONSTRUCTION

- Description:  Laars Electric Tank-Type Water Heater, Model EV.

- Heater shall be vertically oriented.

- Heater diameter shall be:

  - Model EV0150:  32 inches (81 cm)

  - Model ET0200:  32 inches (81 cm)

  - Model EV0250:  34 inches (86 cm)

  - Model ET0300:  40 inches (102 cm)

  - Model EV0400:  46 inches (117 cm)

  - Model EV0500:  46 inches (117 cm)

  - Model EV0600:  52 inches (132 cm)

  - Model EV0800:  52 inches (132 cm)

  - Model EV1000:  52 inches (132 cm)

  - Model EV1250:  58 inches (147 cm)

  - Model EV1500:  64 inches (163 cm)

  - Model EV2000:  70 inches (178 cm)

  - Model EV2500:  76 inches (193 cm)

- Heater height shall be 80 inches (203 cm).

- The heater shall have a painted steel jacket.  The jacket shall be coated on both sides and have a durable finish for maximum protection.

- The heater tanks shall be covered with high-density open cell foam insulation used to meet ASHRAE 90.1b, allowing for maximum 4 Watts per square foot of tank surface energy loss.

- Heater tank shall be double-glass lined with a coating that produces a superior, resistant, long-lasting material that bonds to the steel substrate.  Lining shall be 20 mils thick (+/- 4 mils).Lining shall be able to withstand temperatures up to 180°F (82°C), and shall feature antimicrobial product protection to help prevent the growth of bacteria, mold and mildew on the surface of the tank lining.  The glass lining shall be tested under the following ASTM testing guidelines:

  - Degradation:  W-H-196 Test = 7.0 – 8.0 mg/in2.

  - Resistance:  PEI T-21 Spot Acid Test = Class A.

  - Adhesion:  Impact Resistance = Class 4 to 5.

  - Hi-Pot Test:  Less than 20.

- Heater shall be built with an electrical panel that has a hinged door with keyed lock.

- Heater shall be built with lifting lug access.

- Heater shall be constructed with a channel iron skid base.

- An inspection opening shall provide easy access to the heater interior for inspection and cleaning.

- Low watt density incoloy elements shall be used.  This tough alloy resists the effects of prolonged high operating temperatures, hard water, acids, corrosion, and thermal shock.

- All elements and circuits shall be internally fused in 48 Amp increments, providing complete electrical protection.  Cartridge type ruses shall be rated at 200,000 Amp interrupting capacity.

- Heater shall use magnetic contactors with immersion thermostats.

- The control circuit shall be 120V, with built-in transformer.

- Elements shall be thermostatically controlled in 54kW maximum increments.

- Heater shall have a digital temperature display, located on the front of cabinet.

- Heater shall be equipped with a manual reset high water temperature limit.

- Terminal block connections shall be used, for easy and safe wiring connections.

- Heater shall be equipped with an installed temperature and pressure relief valve.

- Outlet and inlet water connections shall be:

  - 150-250 gallon:  1-1/2” NPT

  - 300-500 gallon:  2” NPT

  - 600-1000 gallon:  2-1/2” NPT

  - 1250-2500 gallon:  3” NPT

- Heater shall be equipped with a drain.

- Heater tank shall include magnesium anode rods, quantities and placement chosen to best protect the tank.

2.3 OPTIONS

- The heater shall be available with the following options:

  - BMS contacts for connection to a building automation system.

  - Low water cutoff to prevent energizing of the heater when not filled with water, or upon a low water condition.

  - Pilot lights and manual limiting switches permit manual limitation of heating input by switching off current to each contactor.

  - Alarm bell for audible alarm.

  - Shunt trip disconnect that provides maximum protection by interrupting all power to the system in the event of a control sensed malfunction or over current (mounted separately).

  - Low pressure switch that turns off control circuit when water pressure drops below a set minimum.

  - High pressure switch that turns off control circuit when water pressure exceeds a set maximum.

  - Electric step controller for electronic sequencing of thermostats (36kW and higher).

  - 7-day clock to control off/on cycles of the heater as programmed by the owner or electric utility requirement.

  - 24-hour clock to control on/off cycles in 24-hour cycles.

  - Safety door interlock that prevents opening of access door while heater is energized.

  - Pressure gauge that is jacket mounted for convenient viewing.

  - 12-inch x 16-inch manway that provides means to easily remove sediment from heater (available on 300 gallon heater).