Laars Heating Systems Company – Stainless Steel 80-115 Gallon Storage Tanks

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes glass-lined, insulated and jacketed domestic water storage tanks.

ACTION SUBMITTALS

Product Data: For each type of product, include rated capacities, operating characteristics, and furnished specialties and accessories.

Sustainable Design Submittals:

Product Data for storage tank insulation.

INFORMATIONAL SUBMITTALS

Coordination Drawings: Equipment room drawing or BIM model, drawn to scale, on which the items described in this Section are shown and coordinated with all building trades.

Product Certificates: Where applicable.

Source quality-control reports.

Field quality-control reports.

Warranty: Standard warranty, shown below.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: Installation and maintenance manual for storage tanks.

COORDINATION

Coordinate sizes and locations of any necessary bases with actual equipment provided.

WARRANTY

Manufacturer’s Warranty: Manufacturer agrees to repair or replace components of storage tanks that fail in materials or workmanship within specified warranty period.

Failures include, but are not limited to, the following:

Structural failures.

Deterioration of metals, metal finishes, and other materials beyond normal use.

Warranty Periods: Limited warranty runs from date of installation (or without proof of installation, from three (3) months after the date of manufacture).

Tank Failure:  5 years.

Other Parts:  1 year.

PRODUCTS

PERFORMANCE REQUIREMENTS

ASHRAE/IES Compliance: Meet or exceed the minimum requirements of ASHRAE/IES 90.1.

COMMERCIAL POTABLE WATER STORAGE TANKS

Basis-of-Design Product: Subject to compliance with requirements, provide Laars Heating Systems Company model LSSJ stainless steel commercial water storage tank, or comparable product by one of the following:

Lochinvar, LLC.

RBI; A Division of Mestek, Inc.

Thermal Solutions LLC.

Raypak, Inc.

Source Limitations: Obtain storage tanks from single source from single manufacturer.

Construction:

Tank Interior:  316L stainless steel construction.

Insulation:  Non-CFC foam R-16 insulation covering the sides and top of the tank.

Jacket:  UV stable thermoplastic jacket.

Outdoor Placement:  Jacket design to all for placement outdoors without the need for additional kits or jacket items.

Water Connections:  2” NPT side water connections.

T&P Relief Valve Opening:  1” NPT tapping on side of tank.

Drain Valve:  Low restrictive brass drain valve with tamper-proof design place in the front of the tank for ease of servicing.

Thermowell:  Stainless steel, removable well.

Temperature Rating:  Storage of potable water up to 180°F (82°C).

Pressure Rating:  150 psi (1034 kPa) working pressure.

Capacity and Characteristics:

Storage Capacity:

LSSJST80C5:  80 gallons (303 liters).

LSSJST115C5:  115 gallons (435 liters).

Overall Height:

LSSJST50C5:  71.5 inches (182 cm).

LSSJST115C5:  71.5 inches (182 cm).

Diameter:

LSSJST50C5:  23.5 inches (60 cm).

LSSJST115C5:  27.5 inches (70 cm).

SOURCE QUALITY CONTROL

Tank must be factory tested for safety and functionality; results recorded for future reference.

EXECUTION

DOMESTIC-WATER HEATER INSTALLATION

Install tanks level and plumb, in accordance with layout drawings, original design, and referenced standards. Maintain manufacturer's recommended clearances. Arrange units so devices needing service are accessible.

Assemble and install any additional or optional trim.

Fill tanks with water.

PIPING CONNECTIONS

Comply with requirements for domestic-water piping specified in Section 221116 "Domestic Water Piping."

Drawings indicate general arrangement of piping, fittings, and specialties.

Where installing piping adjacent to fuel-fired, domestic-water heaters, allow space for service and maintenance of water heaters. Arrange piping for easy removal of domestic-water heaters.

IDENTIFICATION

Identify system components. Comply with requirements for identification specified in Section 220553 "Identification for Plumbing Piping and Equipment."

FIELD QUALITY CONTROL

Perform tests and inspections in accordance with manufacturer’s written instructions.

Tests and Inspections:

Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

Test safety devices. Replace damaged and malfunctioning devices.

Tanks will be considered defective if they do not pass tests and inspections.

Prepare test and inspection reports.