Laars Tankless Electric Water Heaters, Powered by Keltech™

G Series (Formerly C1N Series)

Guide Specification

Laars Tankless Electric Water Heaters, Powered by Keltech™ Light Industrial Water Heaters are designed to accommodate most light industrial fluid heating applications, where the demand is 18kW - 25kW and total flow is 0.75 GPM (2.8 l/m) up to 15 GPM (56.8 l/m). Standard units feature ≥ 0.75 GPM (2.8 l/m) activation, and lower flows are available. G Series (Formerly C1N Series) units are 3 Phase Delta, 480V or 600V. Low flow activation options at 0.25 GPM (1.0 l/m) and 0.50 GPM (1.9 l/m) are available. NEMA 4X and explosion proof purge system options are available.

Available for wall- or floor- mounting, Laars Tankless Electric Water Heaters, Powered by Keltech™ Tankless Light Industrial Water Heaters range from 18 to 25 kW units. They feature shuttle type flow switches that activate a PID controller. Water heaters are equipped with Incoloy 800 sheathed low watt density heating elements and a three-mode (PID) controller with dual digital display of set-point and output water temperature.

Laars Tankless Electric Water Heaters, Powered by Keltech™ Light Industrial water heaters allow water supply to quickly reach the required setpoint temperatures, up to 160 deg. F (71.1 Deg. C) in as little as 20 to 30 seconds and provide a consistent flow of hot water – up to 15 GPM (56.8 l/m) continuously.

Redundant Control and Safety Features: Every Laars Light Industrial water heater includes multiple safety features including internal fusing, digital microprocessor-based temperature control, and splash proof NEMA 4 water tight enclosures. Safety only circuits monitor for over-temperature conditions and ensure output temperature does not exceed maximum water heater allowable working water temperature.

Section 22 11 19 - DOMESTIC WATER PIPING SPECIALTIES (Thermostatic mixing valves)

Section 22 33 13 - INSTANTANEOUS ELECTRIC DOMESTIC WATER HEATERS 
(Laars Tankless Electric Water Heaters, Powered by Keltech™)

Section 22 42 16.11 - COMMERCIAL SINKS AND FAUCETS

Section 22 42 23 - COMMERCIAL SHOWERS AND SHOWER VALVES

Teflon® is a registered trademark of E. I. du Pont de Nemours and Company

©2021, Laars Heating Systems Company, USA. All rights reserved.

SECTION 22 33 13 – INSTANTANEOUS ELECTRIC DOMESTIC WATER HEATERS

- GENERAL

      - SECTION INCLUDES

        - Tankless, electric light industrial water heaters and water heater accessories.

Specifier: If retaining optional "Related Sections" article, edit to include sections applicable to Project.

      - RELATED SECTIONS

        - Division 22 Section "General-Duty Valves for Plumbing Piping" for valves.

        - Division 22 Section "Domestic Water Piping" for water piping.

        - Division 22 Section "Domestic Water Piping Specialties" for vacuum breakers, water pressure-reducing valves, water-hammer arresters, and specialty valves.

        - Division 26 Sections for electrical power and control wiring.

Specifier: If retaining optional "References" article, edit to include standards cited in edited Section.

      - REFERENCES

        - General: Applicable edition of references cited in this Section is current edition published on date of issue of Project specifications, unless otherwise required by building code in force.

        - American National Standards Institute (ANSI): www.ansi.org:

          - ANSI Z21.22 - Relief Valves for Hot Water Supply Systems

        - American Society of Heating, Refrigerating, and Air-Conditioning Engineers https://ashrae.org/

          - ASHRAE/IESNA 90.1 - Energy Standard For Buildings Except Low-Rise Residential Buildings

        - American Society of Sanitary Engineering (ASSE): www.asse-plumbing.org

          - ASSE 1003 - Performance Requirements for Water Pressure Reducing Valves for Domestic Water Distribution Systems

          - ASSE 1010 - Performance Requirements for Water Hammer Arresters

        - Canadian Standards Association/CSA Group (CAN/CSA): www.csagroup.org/us/en/home:

          - CSA-C22.2 No. 88 - Construction and Test of Industrial Heating Equipment

        - National Electrical Manufacturers Association (NEMA) www.global.ihs.com:

          - NEMA Standards Publication 250 - Enclosures for Electrical Equipment (1000 Volts Maximum)

        - National Fire Protection Association (NFPA) www.nfpa.org:

          - NFPA 70 - National Electrical Code

          - NFPA 496 - Standard For Purged and Pressurized Enclosures for Electrical Equipment

        - NSF International (NSF): www.nsf.org:

          - NSF 61 - Drinking Water System Components – Health Effects

          - NSF 372 - Drinking Water System Components - Lead Content

        - Underwriters Laboratories (UL) www.ul.com:

          - UL 50E – Enclosures for Electrical Equipment, Environmental Considerations

          - UL 499 - Standard for Electric Heating Appliances

      - ACTION SUBMITTALS

        - Product Data: For each product:

          - Manufacturer's data sheets indicating unit performance and compliance with requirements.

          - Include details of electrical and mechanical operating parts.

          - Show mounting and securing requirements and utility connection requirements.

Specifier: Retain "LEED Submittals" Paragraph and corresponding "ASHRAE/IESNA Compliance" Paragraph under Quality Assurance Article below for LEED projects.

        - LEED Submittals

          - Product Data for Prerequisite EA 2 Minimum Energy Performance: Documentation indicating that units comply with applicable requirements in ASHRAE/IESNA 90.1, Section 7, "Service Water Heating."

      - INFORMATION SUBMITTALS

Specifier: Retain paragraphs below when Project requirements include compliance with Federal Buy American provisions.

        - Buy American Act Certification: Submit documentation certifying that products comply with provisions of the Buy American Act 41 U.S.C 10a – 10d.

        - Source quality-control test reports.

        - Field quality-control test reports.

      - CLOSEOUT SUBMITTALS

        - Operation and maintenance data.

      - QUALITY ASSURANCE

Specifier: Retain "ASHRAE/IESNA Compliance" Paragraph for LEED projects and for other projects where compliance is required by authorities having jurisdiction.

        - ASHRAE/IESNA Compliance: Applicable requirements in ASHRAE/IESNA 90.1.

        - Source Limitations: Obtain tankless electric water heaters through a single source from a single manufacturer.

        - Electrical Components: Listed and labeled per NFPA 70, Article 100, by a testing agency acceptable to authority having jurisdiction.

        - Sanitation Standard: Comply with NSF 61 for fixture components in contact with potable water.

        - Lead-Free Construction: Comply with NSF 372 for fixture components in contact with potable water.

      - WARRANTY

        - Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of electric, domestic-water heaters that fail in materials or workmanship within specified warranty period.

          - Warranty Period: From Date of Substantial Completion

            - Electrical Components: Two years.

            - Heating Elements: Four years.

            - Heat Exchanger Free From Leaks: Eight years.

- PRODUCTS

      - MANUFACTURERS

        - Basis-of-Design Product: Subject to compliance with requirements, provide Laars tankless electric Light Industrial water heaters, Powered by Keltech™, Rochester, NH. Phone: (603) 335-6300, Web site: laars.com

          - Submit requests for substitution in accordance with Instructions to Bidders and Division 01, General Requirements.

      - TANKLESS, ELECTRIC LIGHT INDUSTRIAL WATER HEATERS

Specifier: The Laars, Powered by Keltech™, G Series (Formerly C1N Series) includes automatic reset and manual reset controls to disable the water heater if the water temperature increases to 175 deg. F (79.5 deg. C).

        - Tankless Electric light industrial water heater, UL 499, sized for constant temperature duty to conform to flow requirements and maintain temperature setpoints up to 160 deg. F (71.1 deg. C), with PID Controller, liquid-cooled solid-state relays, and flow activation.

          - Basis of Design Manufacturer/Model: Laars, Powered by Keltech™, G Series (Formerly C1N Series) Light Industrial Water Heater.

Specifier: Select one of two "Enclosure" subparagraphs.

          - Enclosure: UL 50E [0.063-inch/16-ga.- (1.59-mm-) thick, NEMA 4] [0.063-inch/16-ga.- (1.59-mm-) thick stainless steel NEMA 4X].

          - Enclosure: UL 50E and NFPA 496 Explosion Proof, Class 1/Division 2: [0.063-inch/16-ga.- (1.59-mm-) thick, NEMA 4] [0.063-inch/16-ga.- (1.59-mm-) thick stainless steel NEMA 4X].

            - Mounting: [Wall mounted] [Floor mounted with leg kit].

          - Heat Exchanger: Copper tubing with brazed brass fittings and large internal passageways for minimal pressure drop. Provide NSF 61 barrier materials approved for potable water, without storage capacity.

Specifier: Retain lining and coating options below as required for deionized water or corrosive liquid processing requirements.

            - PFA-Teflon-lined Coating: FDA approved for deionized water or mild corrosive	 fluid applications

            - Xylan Fluoropolymeric Coating: FDA approved for food contact or deionized water

          - High Temperature Package: [Insert temperature required between 160 and 190 deg. F] [Not required].

          - Connections: 3/4 inch NPT (DN 19) inlet, outlet.

          - Pressure Rating: 150 psig (1035 kPa).

          - Flow Turn-On Point: [0.75 gpm (0.49 l/s)] [0.5 gpm (0.32 l/s)] [0.25 gpm (0.016 l/s)].

          - Heating Element: Incoloy 800 sheathed low-watt density resistive element.

          - Temperature Control: Microprocessor with PID logic and dual display of set-point and actual outlet water temperature.

          - Safety Controls:

            - Internal thermostat with auto reset high- limit switch

            - Surface mounted bi-metal thermostat with manual reset

            - Internal Fused Disconnect: [Required] [Not required].

            - Ground Fault Equipment Protection. For leakage to ground, greater than 1 amp, Door-mounted ground fault status light and reset: [Required] [Not required].

          - Capacity:

Specifier: If temperature rise/flow rate data appear on Drawings, then select "As scheduled" option. Otherwise, insert temperature rise and flow rate below from product data sheet. Temperature rise range available: 10 – 140 deg. F (6 – 78 deg. C). High Temperature Option Setpoints Available: 160 - 190 deg. F (71.1 – 87.8 deg. C). Flow range available: 0.75 - 15 gpm (1.9 - 57 L/m).

            - Temperature Rise at Flow Rate: [___ deg F (__ deg C) at ___ gpm (__ L/m)] [As scheduled].

            - Adjustable Temperature Setpoint: [___ deg F (___ deg C)] [As scheduled].

          - Electrical Characteristics: [18] [25] kW at [480VAC/3-phase/3-wire] [600VAC/3-phase/3-wire] [As scheduled].

Specifier: Retain one or more of the following three subparagraphs that describe available options for the G Series (Formerly C1N Series) models.

          - Facility Controls Integration:

            - 4-20 mA input

            - RS-485

            - Process Temp Alarm

      - WATER HEATER ACCESSORIES

        - Provide tankless electric water heater system including the following system accessories

Specifier: Retain accessories required for project from those in subparagraphs below; coordinate with contents of other Division 22 sections.

          - Pressure and Temperature Relief Valves: Pressure and Temperature Relief Valves: [Brass] [Stainless steel, ASME rated and stamped pressure relief valve]. Adjust to pressure setting less than water heater working-pressure rating.

            - Pressure and Temperature Safety Relief Valve set to 80 psig (552 kPa).

          - Pressure-Reducing Valves: ASSE 1003.

          - Vacuum Relief Valves: ANSI Z21.22/CSA 4.4.

          - Shock Absorbers: ASSE 1010 or PDI-WH 201, Size A water hammer arrester.

          - Thread Adapters: NPT to BSPP, stainless steel.

          - Y-Strainer: [Lead Free Brass] [Stainless steel].

- EXECUTION

      - INSTALLATION

        - Tankless, Electric, Domestic-Water Heater Mounting:

          - Install water heaters in accordance with manufacturer's written instructions.

          - Install water heaters level and plumb, according to layout drawings and referenced standards. Insert metal shims as required to level unit and anchor to structure as recommended by manufacturer.

Specifier: Retain subparagraph below for applications where seismic design of component fastening to structure is required by authorities having jurisdiction. Consult project structural engineer for performance requirements.

            - Anchor unit in accordance with Project seismic design requirements.

          - Maintain manufacturer's recommended clearance and access dimensions.

        - Install water supply piping to each water heater, and from heater to fixture requiring hot water supply connection.

          - Install stop valves on water supply and outlet piping. Provide stop valve on each supply in readily-serviced location. Lock stop valve in OPEN position.

          - Comply with Division 22 Section, General-Duty Valves for Plumbing Piping, for stop valve requirements.

        - If shipped loose, install pressure and temperature safety relief valves on water heater. Manifold relief valve discharge as shown in manufacturer's written instructions.

Specifier: Select one of the two following paragraphs, as required by project conditions.

        - Extend relief-valve outlet line, and discharge by positive air gap above closest floor drain.

        - Install relief valve drain piping as indirect waste to spill by positive air gap into open drains or over floor drains. Install hose-end drain valves at low points in water piping.

        - Run relief valve drain piping without creating tripping hazard.

Specifier: Retain accessories in following paragraph that are required for project; coordinate with contents of other Division 22 sections.

        - Install [pressure-reducing valve with integral bypass relief valve in water heater cold water inlet piping] [and] [water hammer arrester in water-heater outlet piping], maximum outlet pressure [___ psig (___ kPa)] [as scheduled].

      - FIELD QUALITY CONTROL

        - Do not energize water heater until hydrostatic testing of domestic water lines is complete. See Division 22 Section "Domestic Water Piping."

        - Test and adjust installation.

          - Set field-adjustable temperature set point of temperature-actuated controls. Adjust set point within allowable temperature range.

          - Replace defective or malfunctioning controls and equipment.

        - Clean unit surfaces, test fixtures, and leave in ready-to-use condition.

END OF SECTION